TABLE OF EQUIPMENT

The below table of equipment is for a single-level underground command and control communications facility supporting personnel and van-sized vehicles in a drive-through setup. Vehicles enter one portal and exit via the other, optimizing flow with a linear layout: ~200-500m long tunnel section for straight-through access, flanked by personnel zones (command and control rooms, communications rooms, and support spaces). Total footprint: ~15,000 – 25,000 square feet (1,395 – 2325 square meter) with enhanced linear ventilation/power runs. Focus should be on critical components (power, HVAC, water distribution systems).

- Structural Support and Hardening

- Reinforced concrete structures and/or panels

- Fortify linear tunnel walls, portals, and shafts; supports vehicle traffic loads

- 18-24” (460 – 600 mm) thick with linear reinforcements for hardened protection and vehicle passage.

- Secure entry/exit for drive through

- Dual portals enable quick ingress/egress

- Type of equipment: hardened portals, security doors

- Vehicle Accommodation

- Guide rails to facilitate entry/exit

- Designated parking or maintenance area for vehicle without blocking traffic flow.  Single lane, parallel parking Provisions for minimum of 8 parking spots inside the underground facility.

- Type of Equipment: underground specific personnel vehicles; diesel or electric.

- Carbon monoxide detection system.

- Provide bollards and barriers inside the facility around critical equipment to protect them from vehicle damage.

- Ventilation and Environmental Control

- No apparent air filtering, possibly on intake ventilation duct or HVAC supply

- Ventilation distributed linearly. Fresh air intake, HVAC supply to generator room, exhaust from generator room to shaft.

- Fresh air intake on East portal, Exhaust from shaft

- Type of equipment: HVAC system equipment (air handling unit with supporting chilled water and condenser water pumps) with dehumidifiers for climate control; 10,200+ CFM capacity, 115kW refrigeration with dampers.

- Provide stainless steel sheet metal ducts per ASHRAE requirements for air distribution.  Provide copper and/or HDPE piping for hydronic systems.

- Provide supply and return air diffusers and grills as needed for air supply and distribution inside the underground facility.

- Provide fresh air for a maximum of 25 persons in the underground facility in accordance with ASHRAE Standard 62.1 – Ventilation for Acceptable Indoor Air Quality.

- Provide a minimum of four air changes per hour for work areas inside the facility

- Local electronic control system with redundant unit.  Provide additional redundant pneumatic control system for control in event of total electronic failure.

- HVAC provisions for this underground facility should support 24/7 operation and follow applicable guidance from

- Power, lighting, and backup systems

- 500kWh total of Uninterruptible power supply (UPS) with batteries collocated near generator room

- Diesel generator to power entire layout, no line power.

- Generator is diesel, mission critical 1875kVA @ 60 Hz, tier 2, air cooled

- Power distribution throughout

- Both standard lighting and emergency lighting throughout

- Provide integral fuel storage for generator system to support the facility for a maximum of 14 days at full load.

- Linear enclosures for radio frequency shielding.

- Electrical for this underground facility should support 24/7

- Lighting for this underground facility should support 24/7

- Communication and Command

- Provide secure radio transceivers (HF/VHF/UHF) powered from generator, cooling from tunnel air movement only.

- Radio room located at base of shaft

- Provide linear antenna runs for vehicle and facility communications

- Connections to exterior antennas routed through utility shaft openings for the underground facility.

- Provide satellite phones and network (Starlink or similar system)

- Provide encrypted video conferencing systems

- Provide protected distribution system (PDS) pathways for secure networks

- Provide commercial telecommunications service to the facility to support telecommunications needed.

- Situational Awareness, Monitoring, and Security

- Provide multi-screen command consoles (Operation center co-located with generator)

- Provide CCTV cameras and sensors for complete video surveillance system.

- Provide intrusion detection system (IDS), access control systems (ACS) turnstile w/card reader for access and personnel accountability

- Type of equipment: SCADA system for: access control, security, environmental and HVAC, fire detection and suppression, power and emergency power monitoring

- Operational Tools and Support

- Centralized accessible storage rack

- Portable generators and tool kits

- Type of equipment: Provisions for fixed and remote charging for stationary and mobile tools provided in controlled and conditioned environment via HVAC and exhaust fans.

- Radio electronic tools include trouble shooting bench with: dummy loads, final end test equipment, including spectrum analyzer and power meter for power modulation of radio.

- Water and Waste Treatment

- Pipes and Pumps to support the following

- Redundant commercial domestic water supply to the underground facility via buried underground piping system.

- On-site water treatment for the underground facility for drinking water (reverse osmosis system).

- Sanitary water / gray water collection system.

- Packaged submersible pumps for sanitary systems (sumps) with electrical wiring, junction boxes, and pump housing.

- Drainage channels

B. Waste Removal

Waste lines and chutes

- External sewage discharge and collection points.

- Sewage system piping with AWWA standard ductile iron or HDPE pipe

- Buried sanitary and sewage system, holding areas for waste via network of underground sewage vaults and/or tanks.

- Packaged sewage ejector pumps for removal of sewage from vaults and tanks.

- Fire Suppression and Fire Alarm Systems

- Provide fire detection and suppression system for the entire underground facility with incoming commercial water supply from municipal or city water supply.

- Provide life safety egress plans for the underground facility

- Provide fire sprinkler systems for dedicated facilities inside the underground facility with network of fire suppression piping, fire pumps, fire hydrants, sprinklers and sprinkler heads.

- Pressurized pipes running along the ceilings, walls, or floors

- Fire suppressions system storage tanks (foam and/or water) with valves, pumps, and control panels

- External hydrants and/or foam dispensers

- Localized fire alarm (FA) and mass notification (MNS) system with FA/MNS control panels, annunciator panels, audible and visual notification devices, and controls.  Fire alarm system interconnected to the SCADA and security systems.

- Terrain

- Fresh granite rock no signs of weathering, no soil covering

- Portal elevation above mean sea-level (MSL) are 1290m West and 1295m East

- Excavation method: drill and blast

- Rock density: 2,700kg/m3, geothermal gradient 2K/100m

- Generator room at 20m depth from surface